Report on Dug Wells implemented by DCH

2nd Phase

## Drinking Water Supply through Pipelines at the Household Level for the Rural Community

Planned and Implemented

#### By

# Dhaka Community Hospital (DCH)

190/1 Baro MoghBazar, Dhaka-1217

Tel: 9351190-91, 8314887

# E-mail: dch@bangla.net

CONTENTS

- Introduction

  - Arsenic Problem – Situation of Bangladesh

1.2 Hazards of Arsenic Intake

1.3 Arsenic Mitigation Programme of DCH

1.4 Wilson Arsenic Mitigation Program

- Brief Description of Dug Well

2.1 Materials Required for Digging and Constructing a New Dug Well

2.2 Installation of Dug Well with Pipeline

2.3 Cost of Digging Dug Well with pipeline

2.4 Maintenance Procedure

2.5 Maintenance Cost

- Project Implementation

3.1 Community mobilization

3.2 Committee formation

3.3 Training of community worker and caretaker

3.4 Site selection

3.5 Drawing of water supply network

3.6 Installation of dug well and pipe network

3.7 Community meeting

3.8 Monitoring

- Proposed 3rd Phase of Mitigation Programme

- Discussion

- Recommendation

- Acknowledgements

Annexure 1   Schematic of the piped water supply system

Annexure 2   Map of the Pabna district showing the location of the wells

Annexure 3   Instructions on how to dig and maintain a sanitary well

Annexure 4   Map of an individual village (Babul Chara)

ANNEX 5   range of costs for dugwells (in the Pabna region)

1. Introduction

  - Arsenic Problem – Situation of Bangladesh

Arsenic contamination in groundwater and its toxic effect on human health is a major public health problem in Bangladesh. In Bangladesh around 97% of the people are dependent on water supply from the groundwater source at present. For more than 30 years tube wells have been introduced for safe drinking water and domestic purposes on a mass scale. But recently the arsenic contamination in groundwater has made this source unsafe. This has created major problems, especially among the rural people. So far 61 districts out of 64 districts are affected with arsenic contamination in groundwater. It is estimated that about 85 million people in Bangladesh are at risk of arsenic toxicity.

All the tube wells in Bangladesh have not yet surveyed. Only about 10-15% tube wells have been surveyed and found that 70% and 40% tube wells have arsenic level above the World Health Organization (WHO) and Bangladesh water quality standard of 0.01 and 0.05 mg/l respectively (DCH, 1998; DPHE, 1997). In some villages 100% of tube wells are contaminated with high level of arsenic.

  - Hazards of Arsenic Intake

Severe health effects have been observed in populations drinking arsenic-rich water over long periods in countries worldwide. The symptoms and signs that arsenic causes appear to differ between individuals, population groups and geographic areas. Arsenicosis - the clinical syndrome originating from high dose arsenic poisoning ranges from spotted melanosis (skin pigmentation) and keratosis (thickening of skin of palm/ foot) up to carcinoma.    In Bangladesh keratoses of the foot often lead to gangrene which, if untreated, can lead to death.

Long-term exposure to arsenic through drinking water causes cancer of the skin, lungs, urinary bladder, and kidney, as well as other skin changes such as pigmentation changes and thickening (hyperkeratosis) gangrene of limbs.

Arsenicosis patients suffer also socially and culturally. Youths are refused marriage, many women and some men have been divorced and children are often asked to leave school. It is also important to non that no proper case management a arsenicosis case for prevalence was been under taken by government, or non government agencies. DCH also with is limited resources trying to case for the arsenicosis patients.

  - Arsenic Mitigation Programme of DCH

DCH has been involved with the arsenic problem since 1996 when DCH doctors working at an annual health camp at Pakshi, Pabna District first detected patients suffering symptoms of arsenicosis.  DCH lobbied extensively to establish this issue as a public health problem and went on to work with Jadevpur University, Kolkata to sample survey the whole of Bangladesh.  Since then it has collaborated with various partners in research into the problem and solutions for mitigation as well as conducting its own arsenic projects.  DCH also provides training on arsenicosis and arsenic problems through its Institute of Family Health, including training for oversees medical personnel e.g. The Nepalese Health Department.

  - Wilson Arsenic Mitigation Program

For the last few years DCH has been implementing on arsenic mitigation programme with financial assistance obtained by Prof. Richard Wilson, Department of Physics, Harvard University, USA.  In the first phase of the mitigation programme, DCH renovated and installed 43 dug wells (including one with pipeline supply system). This phase covered 631 families – serving 3250 users. In the second phase, 17 dug wells with pipeline network were installed which covered 518 families – serving 2903 users.

In this process approximately 100 arsenicosis patients are getting arsenic free safe water. These patients are getting regular checkup by experienced doctors and it appears that they are improving.

2. Brief Description of Dug Well

Dug well is thousand years old technology of water supply in rural Bangladesh. Almost all the people used this technology before tube well came in. For the past 30 to 40 years hand tube well was promoted on a mass scale and as tube well became very popular source of drinking water and household purpose, dug wells gradually decayed because of non-use. Recently tube wells are found to be contaminated with high level of arsenic all over the country. To mitigate arsenic problem, Dhaka Community Hospital has started to provide dug well and other alternative safe water options (PSF, RWH etc) in the arsenic affected communities in collaboration with GoB and donor agencies. DCH is also providing dug wells with pipeline system in some areas.

### 2.1 Materials Required for Digging and

### Constructing a New Dug Well

1. Spade, Crowbar etc.

2. Nylon rope

3. Bamboo pole

4. Cement ring

5. Sand and cement

6. Bricks or brickbats

Fig: Materials required for digging and

constructing dug well platform

2.2 Installation of Dug Well with Pipeline

As DCH has taken up the programme of dug well, a protocol for safety of dug well construction and keeping dug well water free from contamination was formulated. Later on this protocol was further strengthen by WHO protocol, which is now being followed (Annexure 3).   March and April, driest months in the country, are considered the best time for digging wells.  During this period, ground water remains at the lowest level.

A hole is dug about a diameter of 36 inches. The depth of each well varies from place to place. Cement or baked clay ring is set from bottom to top and joining of rings is cemented to keep the well water safe from contamination. An apron of about four feet is made around the head wall and a 30-40 feet drain is constructed at the ground level to avoid water logging around the head wall.

An electric pump machine pumps water from dug well to an overhead reservoir of 3000 L. Overhead tank is installed on an 15 feet tall iron stand. The stand is fixed on the ground with RCC work. A main water supply pipe (3 /4 '' plastic pipe) is connected with the tank for distribution of water to the household level. 1/2'' GI pipeline is connected with the mainline to supply water at the household. 40-50 households are connected with the supply line.

2.3 Cost of Digging Dug Well with pipeline

Digging a well with pipeline and cementing its floor at the ground level would cost an amount of Tk 85,000/= to 90,000/= The price however, may differ from place to place.

Table 1: Cost of dug well

| Material | Quantity | Price in Tk | Total Tk |
| --- | --- | --- | --- |
| # 1. Cement Ring | 42 | 500 | 21,000 |
| 2. Brick | 800 | 4 | 3,200 |
| 3. Sand | 100 cft | 20 | 2,000 |
| 4. Cement | 5 bags | 400 | 2,000 |
| 5. Brick bats | 20ft | 35 | 700 |
| 6. Labor charge for earth digging | 42 ft | 250(per ft) | 10,500 |
| 7. Cement Bats |  |  | 1,700 |
| 8. Cover of well | 1 |  | 3,500 |
| 9. Bucket & rope |  |  | 600 |
| 10. Others |  |  | 500 |
| Total cost per dug well = 45,700 |  |  |  |

Table 2: Cost of supply line

| Material | Quantity | ## Price in Tk | ## Total Tk |
| --- | --- | --- | --- |
| 1.Water tank | 1 (4000 L) | 10,000 | 10,000 |
| 2.Iron stand | 4 | 1,500 | 6,000 |
| 3.Machine | 1 (1HP) | 6,000 | 6,000 |
| 4. Labour (Pipeline) | 3 | 3,000 | 3,000 |
| 5.Labour (stand set ) | 4 | 600 | 600 |
| 6.Cover | 1 | 1,000 | 1,000 |
| 7. Tank transportation | 1 | 350 | 350 |
| 8.Cement | 3 bags | 400 | 1,200 |
| 9.Brick bats | 7 cft | 35 | 245 |
| 10.Sand | 15 cft | 20 | 300 |
| 11.Coil pipe | 700 ft | 10 | 7,000 |
| 12.1/2 T | 6 | 50 | 300 |
| 13. Elbow (1/2 ) | 10 | 55 | 550 |
| 14. Union | 8 | 65 | 520 |
| 15.jam nut | 10 | 40 | 400 |
| 16.Nipple | 15 | 30 | 450 |
| 17. T | 10 | 45 | 450 |
| 18.Tap | 8 | 100 | 800 |
| 19.Elbow (1) | 12 | 25 | 300 |
| 20.GI pipe ½ | 20 ft | 30 | 600 |
| 21.Brash tap | 10 | 15 | 150 |
| 22.Haback | 250 gm |  | 10 |
| 23.Cheek valve | 1 | 250 | 250 |
| 24.PVC | 4 | 25 | 100 |
| 25.Electric wire | 25 m | 10 | 250 |
| 26.Plague pin | 1 | 10 | 10 |
| 27.Transport |  |  | 300 |
| Total cost of pipeline network per dug well = 41,135 |  |  |  |

1. Cost of dug well per unit 			Tk. 45,700.00

2. Cost of pipe line installation per unit 	Tk. 41,135.00

Grand total 				Tk. 86,835.00 = $1,524 (US)

Note: Calculated using 1 USD ($) = Tk. 57.00 only

Table 3: List of 17 New Dug Wells with Pipeline Installed by Dhaka Community Hospital (DCH) with charitable funds ($20,000.00 (US)) in the 2nd Phase of Mitigation Programme

| Dug well No | Name of Village | Name of Union | Name of upazilla | Name of District | Unit Point | Total Family | Family covered | Total Population of village | Population covered by dug well |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. | Ruppur (Malitha para) | Pakshi | Ishwardi | Pabna | 06 | 65 | 40 | 390 | 240 |
| 2. | Ruppur (Biswaspara) | Pakshi | Ishwardi | Pabna | 06 | 75 | 37 | 450 | 222 |
| 3. | Ruppur(Charabottala) | Pakshi | Ishwardi | Pabna | 08 | 68 | 53 | 408 | 318 |
| 4. | Babulchara | Awtapara | Ishwardi | Pabna | 08 | 70 | 48 | 410 | 340 |
| 5. | Durgapur | Ahammedpur | Sujanagor | Pabna | 07 | 70 | 28 | 420 | 168 |
| 6. | Gopalpur | Kashinathpur | Santhia | Pabna | 06 | 52 | 20 | 312 | 120 |
| 7. | Sayedpur(Dangapara) dug well No- 1 | Ahammedpur | Sujanagor | Pabna | 05 | 65 | 25 | 455 | 125 |
| 8. | Ahammedpur | Ahammedpur | Sujanagor | Pabna | 06 | 28 | 22 | 180 | 130 |
| 9. | Koromja | Koromja | Bera | Pabna | 06 | 35 | 28 | 280 | 140 |
| 10. | Sayedpur(Ujanpar)dug well No-1 | Ahammedpur | Sujanagor | Pabna | 06 | 40 | 30 | 221 | 115 |
| 11. | Sayedpur(Dangapara) dug well No- 2 | Ahammedpur | Sujanagor | Pabna | 06 | 70 | 35 | 400 | 125 |
| 12. | Sayedpur(Ujanpar)dug well No-2 | Ahammedpur | Sujanagor | Pabna | 08 | 47 | 32 | 282 | 192 |
| 13. | Sayedpur(Ujanpar) dug well No-3 | Ahammedpur | Sujanagor | Pabna | 07 | 29 | 24 | 164 | 120 |
| 14. | Sayedpur(Ujanpar) dug well No-4 | Ahammedpur | Sujanagor | Pabna | 06 | 35 | 28 | 290 | 180 |
| 15 | Arippur | Municipality | Pabna | Pabna | 06 | 100 | 15 | 600 | 88 |
| 16 | Bhabanipur | Ruppur | Bera | Pabna | 06 | 154 | 27 | 616 | 150 |
| 17 | Shagorkandi | Masumdia | Bera | Pabna | 05 | 148 | 26 | 596 | 130 |
| Total: Dug well 17 Total: Tap Point 108 Total: Family 1151 Total: Family coverage 518 Total: Population 6474 Total: Population coverage 2903 |  |  |  |  |  |  |  |  |  |

Cost of per unit dug well with pipeline =	Tk 86,835.00

Cost of 17 dug wells with pipeline 	      =	Tk ( 86,835.00x17)

=	Tk 14,76,195

= 	 $25,900 (US)

Note: Calculated using 1 USD ($) = Tk.57.00 only

2.4 Maintenance Procedure

Hardly any expense is required for maintaining

dug well. Well have to be cleaned once in a

year and it may cost an amount of Tk 3000 to

4000. The best time for cleaning is the period

between March and April.

2Kg lime is thoroughly mixed with 35 L of

water and then it is poured in the well. The well

water is stirred and then kept unused for 3 to 4

days. After 3 days the well is unloaded. The

well is then filled with fresh water seeping from

the aquifer.                                                                                           Fig: Maintenance

# 2.5 Maintenance Cost

| Material | Quantity | Price | ## Taka |
| --- | --- | --- | --- |
| Labor charge for cleaning | 3 person | 400 | 2,000 |
| Potash | 100 gm |  | 30 |
| Lime | 3 Kg | 10 | 30 |
| Others |  |  | 1,000 |
| Total = 3,060 = $ 54.00 (US) |  |  |  |

Note: Calculated using 1 USD ($) = Tk.57.00 only

3. Project Implementation

Major activities of this project were as following:

- Community mobilization

- Committee formation

- Training of community worker and caretaker

- Site selection

- Drawing of water supply network

- Installation of dug well and pipe network

- Community meeting

- Water quality monitoring

3.1 Community mobilization

Various mobilization and motivational

activities such as courtyard meeting etc were

conducted to increase public awareness.

Several meetings were held in these villages

with the community. Local Government of

Bangladesh (GoB) elected persons

and influential local people were present in

meetings along with DCH personnel.

Community people including women, the

poor and arsenic patients shared their

situation, needs, opinions and preferences

about mitigation options with others.                                    Fig: Community mobilization

3.2 Committee formation

A committee was formed for the supervision

of each implementation. Each committee was

responsible to maintain the option provided

to them. DCH and the committees worked

together to plan option installation and

maintenance. Committee accepted responsibility

to collect community contribution.

Committee decided the charges for water use

for each family. Caretaker collected money from

water users. Each family was provided with a                        Fig: Committee formation

water card for payment.

3.3 Training of community worker and caretaker

Local mistiris were selected for construction and maintenance of the options. They were

trained on construction work options by DCH trainers. DCH trainers also trained caretakers

and users of options.

3.4 Site selection

Sites of option were selected in highly contaminated areas. This was done after consultation with the community. Preference was given to the patient families and the poor. Sites satisfied guidelines provided for site selection.

3.5 Drawing of water supply network

Drawing of pipeline network and dug well was prepared. The pipeline network ended at household level.

3.6 Installation of dug well and pipe network

Process of the installation was discussed and

shared with the community. The committee

supervised during installation period.

This committee is responsible for maintenance.

Dug well sites were selected in environmental

friendly areas and in arsenic affected population.

Wells were protected from outside contamination.

Dug well water is stored in an overhead tank.

Water is supplied 2 or 3 times through pipeline

at the household level. Villagers paid monthly

fee for maintenance of the system.                                  Fig: Installation of Dug Well with Pipeline

3.7 Community meeting

Meetings with the community were held in

the project areas with the community. Local

GoB elected person and influential local

people were present in meetings along with

DCH personnel. Community people

including women, the poor and arsenic

patients exchanged opinions and identified

their needs.

Fig: Community meeting

3.8 Monitoring

Project activities were monitored by DCH through observations, open interview etc. DCH engineer monitored implementation activities. Clinical survey of water users was carried out per month.

The arsenic level of the dug well water was tested once in DCH after option installation. Bacterial count of dug well water was done at three monthly interval using either the DELAGUA or the  Jaltara field test kit.

4. Proposed 3rd Phase of Mitigation Programme

Drinking water supply from dug well through pipeline network is well received by the communities. This option should be replicated in other arsenic contaminated places. A plan for installing 100 new dug wells with pipe network in contaminated areas is proposed here in the Table – 4.

Table 4: Plan for installing 100 new dug wells with pipeline

(3rd Phase of Mitigation Programme)

| Sl | Name of Village | Name of Union | Name of Upazilla | Name of District | Type of dug well | Quantity | Cost per dug well with pipeline (Taka) | Total cost (Taka) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. | Char Ruppur | Pakshi | Ishwardi | Pabna | New | 05 | 86,835/= | 4,34175/= |
| 2. | Billkanda | Shahapur | Ishwardi | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 3. | Laksmikunda | Shahapur | Ishwardi | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 4. | Babulchara | Shahapur | Ishwardi | Pabna | New | 02 | 86,835/= | 1,73635/= |
| 5. | Kolerkandi | Selimpur | Ishwardi | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 6. | Shekherdari | Selimpur | Ishwardi | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 7. | Baghoil | Pakshi | Ishwardi | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 8. | Birahimpur | Ahmmadpur | Sujanagar | Pabna | New | 02 | 86,835/= | 1,73635/= |
| 9. | Ahmmadpur | Ahmmadpur | Sujanagar | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 10. | Sayadpur | Ahmmadpur | Sujanagar | Pabna | New | 05 | 86,835/= | 4,34175/= |
| 11. | Vatikaya | Ahmmadpur | Sujanagar | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 12. | Shibrambari | Kashinathpur | Shathia | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 13. | Shumashnari | Koromja | Shathia | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 14. | Dariapur | Kashinathpur | Shathia | Pabna | New | 02 | 86,835/= | 1,73635/= |
| 15. | Khuddra gopalpur | Kashinathpur | Shathia | Pabna | New | 02 | 86,835/= | 1,73635/= |
| 16. | Punduria | Koromja | Shathia | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 17. | Ujan kaya | Ahmmadpur | Sujanagar | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 18. | Pagla | Ahmmadpur | Sujanagar | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 19. | Chabbish maill | Ahmmadpur | Sujanagar | Pabna | New | 02 | 86,835/= | 1,73635/= |
| 20 | Goalkandi | Shagorkandi | Sujanagar | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 21 | Raghurampur | Kallanpur | Shathia | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 22 | Shagorkandi | Shagorkandi | Sujanagar | Pabna | New | 02 | 86,835/= | 1,73635/= |
| 23 | Shinduri | Shagorkandi | Sujanagar | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 24 | Bisshanath pur | Jatshakini | Bera | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 25 | Durgapur | Ahmmadpur | Sujanagar | Pabna | New | 02 | 86,835/= | 1,73635/= |
| 26 | Koromja | Koromja | Shathia | Pabna | New | 02 | 86,835/= | 1,73635/= |
| 27 | Akdarpur | Ahmmadpur | Sujanagar | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 28 | Natun ruppur | Pakshi | Ishawardi | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 29 | Mobarokpur | Ahmmadpur | Sujanagar | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 30 | Arippur | Municipality | Municipality | Pabna | New | 02 | 86,835/= | 1,73635/= |
| 31 | Mashumdia | Mashumdia | Bera | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 32 | Oikhali | Kallanpur | Shathia | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 33 | Kolagashi | Kashinathpur | Shathia | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 34 | Balorampur | Kallanpur | Shathia | Pabna | New | 03 | 86,835/= | 2,60505/= |
| 35 | Kallanpur | Kallanpur | Shathia | Pabna | New | 03 | 86,835/= | 2,60505/= |
| Total village: 35 |  |  |  | Total new dug well: 100 |  |  | Total = Tk 86,83,185.00 = $152,340 (US) |  |
| Tk 57.00 = $152,340 (US) |  |  |  |  |  |  |  |  |

5.     DISCUSSION

- The project successfully achieved its implementation targets of seventeen dug wells and pipe networks in Harvard project area in Pabna district, on time and within budget.

- There was a very positive community attitude to seeking alternative water options. The community supported the project and project personnel throughout the implementation period.

- Each committee decided on a contribution of 20 Tk. per household per month from the community and the caretakers are collecting this. The money is used for maintenance and electricity charges for the pump.

- Each committee has taken responsibility for maintaining the option.

- The water column in dug wells at the driest period was 6 to 8 feet. This amount is sufficient to serve the communities.

6.     RECOMMENDATIONS

  - A dug well with pipeline network to the household level is readily acceptable by the community as an alternative to tube wells. A similar implementation programme can be extended to other arsenic contaminated areas. A 3rd phase of this programme is proposed (Page - 9).

  - Community involvement significantly enhances project sustainability through promoting the concept of community ownership of options.  This encourages a positive attitude towards community contribution for the option.

  - Economic contribution should be equitable. Community involvement also guarantees equitable community contribution.

  - Water option should be provided free of cost for the hardcore poor.

  - Some flexibility in project timing is required to take into account any political/institutional instability and the consequent delays this causes.

  - If possible these projects should be timetabled so that dug well installation commences in the dry season thus assisting implementation.

  - Patient management is also an important as part in mitigation activity needs to be address properly.

- ACKNOWLEDGEMENTS

This work was supported by charitable donations from several sources, and in particular the OPEC fund of Vienna, Austria.  Our thanks are due to Professor Richard Wilson of Harvard University for his encouragement and location of these funds.

Annexure 1    Schematic of a piped water system

Annexure 2    Map of Pabna district showing dugwells

Annexure 4   Drawing of an individual village (Babul Chara)

Annexure 3      GUIDelINES FOR CONSTRUCTION

AND MAINTENANCE OF A DUGwell

# A. Dug Well Survey

- Survey and collection of records (number, location, present situation) of any existing DW in the area should be made

- Causes of unused DW should be made

- Attempts should be made to renovate existing DW if possible

- In case of non-availability of any such records, a test borehole should be made to make a bore log at the site.

# B. Site Selection

Site is selected considering factors –

- Areas of peaty soil should be avoided for DW as these cause the water to have an unpleasant taste and smell.

- There should be a stable soil layer at the top (a clay layer is preferable)

- Presence of sandy layer within 9 to 12 m (30-40') from ground level

- The site must be at least 30' away from any existing latrine

- The site must be at least 30' away from pond

- The site must be at least 30' away from a river

# C. Dug Well Configuration

- Inner diameter is 88.2 cm (3') and outer is 1.17 m (4')

- Depth of DW varies with the soil condition and water availability of the site. Depth should be such to ensure 1 to 1.5 m (3' - 6') water column at the driest period

- Height of concrete ring is 29.4 cm (1')

- Height of head wall is 1 m (3.5') above ground level

- About 59 cm (2') apron is provided all around the well

- 1.17 m (4') x 75 cm (2.5') platform is provided for TW installation beside apron

- Length of drain pipe attached with TW platform varies from 1.5 m to 3 m (5' -10')

- DW should be covered to protect it from outside contamination ensuring proper ventilation and sunlight. The cover is made following WHO guidelines. Or a 0.4m (1’4”) wire mesh should be placed on the head wall, for ventilation and a roof on the top with translucent sheet to facilitate illumination and sunlight.

# D. Manpower

- Trained workers (mistris) are used for construction

- 6 workers (mistirs) should be employed for construction work- 1 head mistri, 2 assistant mistris and 3 local persons to help the mistris so that they become trained after construction of a few DW.

# E. Construction

- DW should be dug manually

- DW should not be constructed a pre-specified depth, s required depth will depend on the soil and water table conditions. Instead it is better to construct dug well in the dry season, with the objective of achieving about two meters of water in the DW upon completion. This procedure will ensure a sufficient depth of water to remain serviceable year-round.

- Concrete rings are inserted after completion of digging

- Where the sub-soil formation is not stable enough, the method of caisson driving (widely used in bridge construction), may be used

- Where self-sinking method is used, the first ring of the DW should be robustly fabricated with a cutting edge

- To prevent sand boiling rings should be jointed together using cement mortar inside and outside of rings and joint-less flexible PVC, floating pipe can be connected with TW. Iron rings, connected with concrete rings, can be used to hold this flexible pipe

- To prevent accidents, during construction of DW, due to collapsing of side-soil and occasionally asphyxiation from carbon dioxide and methane gases- rope, ladder, Bosun’s chair etc should be kept at the site. None should be allowed to work alone.

# F. Water Quality

- 30 cm (1') layer of brick chips are placed at the bottom of the well. 1.8 cm or 3/4'' chips are placed at the bottom in 10 cm (4'') layer, 1.3 cm (1/2'') chips are placed in next 10 cm (4'') and 2.5 cm (1'') chips are placed in the last 10 cm (4'').

- Water parameters should be tested in the laboratory at least two times a year. These parameters should be: pH, colour, turbidity, iron, manganese, chloride, total dissolved solids, total coliform, faecal coliform and arsenic.

- Well water is cleaned two times a year. For this 2 kg lime is thoroughly mixed with 35 L of water and then it is poured in the well. The well water is stirred and then kept unused for 3 to 4 days. After 3 days the well is unloaded. The well is then filled with fresh water seeping from the aquifer.

ANNEX 5

About the cost (in dollars)  of the safe,  improved,  dugwells:  the  detail follows:

Cost per renovated dugwell with hand tubewell:(100-150people)   $150-200

Cost per renovated dugwell with pipewater household supply: (average

300-500people) $700-850

New dugwell with tubewell: (100-150 people)   $500-600

New dugwell with pipewater:  (average 300-500people) $1000-1200

These changes are variable due local condition and soil conditions.